| AUTHOR: ITSM2 LOT1 | ISSUE DATE: 16/06/2014 | VERSION: 0.10 |
| --- | --- | --- |
| European Commission Taxation and Customs Union DG SUBJECT: ITS-1MPR-Annex 26-Datacentre Luxembourg Monthly Report 201405 EN |
| SfR |
| This document is to address part of ITSM2 Lot1 contractual commitments described in the document. The report provides for Operational Measurements made by ITSM2 Lot1. |

Table of Contents

1	Document Overview	4

1.1	How this document is organised	4

2	Management Summary	5

2.1	MAY 2014 Summary	5

2.2	Indication of the main activities in the DG TAXUD data rooms	6

2.2.1	Activities in Drosbach	6

2.2.2	Activities in Kayl	6

2.3	MAY 2014 Trends and Remarks	8

3	Availability Management	9

3.1	EDH Drosbach Availability	9

3.2	eBRC Kayl Availability	9

4	capacity Management	10

4.1	Capacity Management Drosbach (following IBM measurements)	10

4.2	Capacity Management Kayl	12

4.3	Manual Power Consumption Measurements	14

5	Environment control drosbach and Kayl	15

5.1	Power Drosbach and Kayl	15

5.2	Humidity Drosbach and Kayl	16

5.3	Temperature Drosbach and Kayl	17

6	Incident Management	18

6.1	Number of Incidents in Drosbach	18

6.2	Number of Incidents in Kayl	18

6.3	Critical Incidents / Emergency Incidents	19

6.3.1	EDH Drosbach	19

6.3.2	eBRC Kayl	19

7	Facility Management	20

7.1	Number of Facility Requests in Drosbach	20

7.2	Number of Facility Requests in Kayl	22

7.3	Number of Equipment Deliveries in Kayl	23

7.4	Number of Equipment Deliveries in Kayl	23

7.5	Number of Access Request Tickets Opened/Closed in Drosbach	24

7.6	Number of Access Request Tickets Opened/Closed in Kayl	25

8	Inventory in Drosbach Storage Room	26

9	Planned Maintenances (DroSbach and Kayl)	28

9.1	Planned Maintenance Activities in Drosbach	28

9.2	Planned Maintenance Activities in Kayl	30

10	Conclusions	32

10.1	Risks from DC Management perspective	32

10.2	High Light/ Low light section	32

10.3	DOCUMENT HISTORY	33

10.3.1	Revision History	33

10.3.2	Approvals	33

10.3.3	Distribution	33

List of tables

Table 21-April Management Summary	5

Table 41-Drosbach Manual Measurements	14

Table 42-eBRC Manual Measurements	14

List of figures

Figure 41-A Drosbach Data Room Plan	10

Figure 41-B-Drosbach Power Usage	11

Figure 41-C-Cooling Usage	11

Figure 42-Kayl Data Room Plan	12

Figure 43-Kayl Yearly Consumption	13

Figure 51-Power Usage Drosbach/Kayl	15

Figure 52-Humidity Usage Drosbach/Kayl	16

Figure 53-eBRC Hygrometry and Humidity Trends	16

Figure 54-Temperature Usage Drosbach/Kayl	17

Figure 61-Incidents in Drosbach	18

Figure 62-Incidents in Kayl	18

Figure 71-Number of Facility Requests In Drosbach	20

Figure 72-Number of Facility Requests in Kayl	22

Figure 73-Number of Deliveries in Drosbach	23

Figure 74-Number of Deliveries in Kayl	23

Figure 75-Number of Access Requests in Drosbach	24

Figure 76-Number of Access Requests in Kayl	25

Figure 81-Inventory in Drosbach Storage Room Movements	27

Figure 91-Planned Maintenances in Drosbach – April 2014	28

Figure 91-Thirteen months rolling forecast	29

Figure 92-Yearly Provider maintenance plans in Kayl	31

# Document Overview

This document is to address part of ISTM2 Lot1 contractual commitments described in the document. The report provides for Operational Measurements made by ITSM2 Lot1.

## How this document is organised

The document contains sections organized as follows:

- Management Summary – High level performance overview;

- Trends and Remarks  - Provides an overview of the highlights/lowlights, trends and issues/comments;

- Availability Management – Contains an overview of Power outages;

- Capacity Management – Provides an overview of the rack capacity and power capacity;

- Environment Control Service level check – Contains an overview of the checks on vital KPI’s of the DC providers (Power / Humidity / Temperature);

- Incident Management – Contains an overview of the total number of opened and closed incidents within the reporting period;

- Facility Management– Provides the total number of Facility requests opened and closed within the reporting period;

- Maintenance;

- Inventory Storage room – Provides the inventory of goods stored at the end of the reporting period.

# Management Summary

## MAY 2014 Summary

| Service | Definitions | Target | February | Results |
| --- | --- | --- | --- | --- |
| 3. Availability Management |  |  | # |  |
| Availability DC room Drosbach | Power outages / reported by EDH | Tier IV | No Incident | 100 % |
| Availability DC room Kayl | Power outages / reported by Ebrc | Tier IV | No Incident | 100 % |
| 4.1 Capacity Drosbach |  |  |  |  |
| Capacity Racks | Free rack positions of total | ≥20% free | 51 racks free | 68,75% free |
| Capacity Power | % Power used of total | ≤55% | 0, 152 kW/sqm | 15,213% |
| 4.2 Capacity Kayl |  |  |  |  |
| Capacity Racks | Free rack positions of total | ≥20% free | 54 racks free | 77,14% free |
| Capacity Power | % Power used of total | ≤55% | 0, 100 kW/sqm | 10, 08% |
| 5.1 Environment Control Drosbach |  |  |  |  |
| 1. Power out of target | Weekly Visual check | Tier IV | No | 100 % |
| 2. Cooling out of target | Weekly Visual check | TBD | No | 100 % |
| 3. Temperature out of target | Weekly Visual check | 22°±2° | No | 100 % |
| 4. Humidity out of target | Weekly Visual check | 50%±10% | No | 100 % |
| 5.2 Environment Control Kayl |  |  |  |  |
| 1. Power out of target | Weekly Visual check | Tier IV | No | 100 % |
| 2. Cooling out of target | Weekly Visual check | TBD | No | 100 % |
| 3. Temperature out of target | Weekly Visual check | 22°±2° | No | 100 % |
| 4. Humidity out of target | Weekly Visual check | 50%±10% | No | 100 % |
| 6.1 Incident Management Drosbach |  | Target | # |  |
| incidents opened | DC facility incidents | NA | 1 |  |
| incidents closed | DC facility incidents | NA | 1 | 100 % |
| Incident/emergency out of office hrs | Out of Office hrs incidents | NA | 0 |  |
| 6.2 Incident Management. Kayl |  | Target | # |  |
| incidents opened | DC facility incidents | NA | 1 |  |
| Incidents closed | DC facility incidents | NA | 1 | 100 % |
| Incident/emergency out of office hr | Out of Office hrs incidents | NA | 0 |  |
| 7.1 Facility Request Drosbach |  | Target | # |  |
| facility requests opened | Requests | NA | 24 |  |
| facility requests closed | Requests | NA | 24 | 100 % |
| 7.2 Facility Request Kayl |  |  |  |  |
| facility requests opened | Requests | NA | 12 |  |
| facility requests closed | Requests | NA | 12 | 100 % |
| 7.3. Equipment Delivery |  | Target | # |  |
| Equipment delivery Drosbach | Deliveries | NA | 5 |  |
| Equipment delivery Kayl | Deliveries | NA | 1 |  |
| 8. Health and Safety |  | Target | # |  |
| Health & Safety incidents Drosbach | Health & Safety incidents | 0 | No |  |
| Health & Safety incidents Kayl | Health & Safety incidents | 0 | No |  |

Table 21-April Management Summary

## Indication of the main activities in the DG TAXUD data rooms

### Activities in Drosbach

01.04.14	  Electricity statement

02.05.14	  Electricity statement

Assignment Asset Tags

05.05.14	  Inventory of free SFP on NS5400 at Drosbach (for <Removed Name>)

Weekly check

07.05.14	  Verify with <Removed company name> if possible to displace coppers in rack D107 and D108 (as asked by dudu66)

08.05.14	  Cabling on M5000 at Drosbach

09.05.14	  Verify inventory for Asset manager

12.05.14	  Preparation for the audit of 16/05

13.05.14	  Weekly check

15.05.14	  Decommission of the temporary switches in the D105 and D106

16.05.14	  Audit <Removed company name>

19.05.14	  Audit activities

21.05.14	  Inventory coppers connections at Drosbach

Conference call with <Removed Team name> about thresholds on CMC's

Weekly check

22.05.14	  Change of the temperature and humidity thresholds on the CMC's

26.05.14	  Installation SSG550M at Drosbach with SY + cabling and test

Displacement of Management switches from row 1 to row 2

28.05.14	 Thermography Control + verification of each lighting system + turnstile by <Removed company name> (Contract with <Removed company name>)

Test with <Removed Team name>

30.05.14	  Electrical statement

Weekly check

### Activities in Kayl

02.05.14	  Electricity statement

Weekly Check

07.05.14	  Install and test fiber trunks between K101 and K210

13.05.14	  Retry all the doubles keys which was in the safe

Weekly Check

16.05.14 	  Audit <Removed company name>)

20.05.14	  Re-cabling of the CMC's at Kayl + test

22.05.14	  Change of the temperature and humidity thresholds on the CMC's

23.05.14	  Change sensitivity on the 6 racks doors which have problem at Kayl

Weekly Check

Conference call <Removed Team name>: DGTAXUD - Validating implement of DCIM control systems in Kayl

26.05.14	  Displacement of Management switches from row 1 to row 2

27.05.14	 Thermography Control + verification of each lighting system + turnstile by <Removed company name>) (Contract with <Removed company name>))

30.05.14	  Electrical statement

Weekly check

## MAY 2014 Trends and Remarks

Principal activities encountered in May 2014, especially concerns LOT3 Audit findings, continuation of solving <Removed product name>)implementation issue, in touch with <Removed company name>)and <Removed company name>) (<Removed geographical localisation> units)

Trends and remarks on:

DC Facility Management

- Some action points have been continued by IBM TAXUD DCM

- Interaction  between <Removed company name>)and <Removed company name>)to finalize a solution concerning <Removed product name>)installation issue and <Removed product name>)Implementation (<Removed Nominative information>)

Issue solved concerning large majority of <Removed product name>)’s but it stays around 6 units to be replaced due a production failure at <Removed product name>) level.

- <Removed company name>) audit realized on 16.05 in both sites. (Final reporting is awaited)

- Continuation of optimization measurements (awaiting a global DG Taxud decision after reception of <Removed company name>)final offering).

- Fixed a solution and a planning to solve the problem of <Removed product name> implementation at Kayl  after reordering in a first step:

- Are awaiting from <Removed product name> 6 new <Removed product name> to finalize issue solving.

-	Once issue will be completely solved, <Removed company name>) will finalize implementation of <Removed product name> (no additional charge to be considered)

-	A half day of training is foreseen when solution will be validated.

Remarks on:

- Health and Safety

No remarks this month

- Critical incidents  / emergencies

No remarks this month

- Recurrent incidents  / emergencies

No remarks this month

# Availability Management

## <Removed company name>)Drosbach Availability

There were no Power outages during the month of May 2014.

## <Removed company name>)Kayl Availability

There were no Power outages during the month of May 2014.

# capacity Management

## Capacity Management Drosbach (following <Removed company name>)measurements)

- Overview of racks used / free (physical)

Surface is 199, 93 sqm’s – 75 Racks (24 used / 51 free) - 31, 25% used

Figure 41-A Drosbach Data Room Plan

- Power / Cooling capacity available

- Power

DC1 TAXUD IT Room “502.A1” is powered to N+N and is dual corded or utilises in rack Static Switches (STS).

Maximal power distribution is 1.000 W/sqm.

April Monthly Consumption = 20.045, 00 kWh (April = 720h/month)

May used power: (22.629, 00 kWh/744h)/199.93 = 0, 1521 kW/sqm, 30,42 kW or 15, 21%

- Cooling

3 x 80kW AHU’s on the feed “A” and 3 x 80kW AHU’s on the feed “B”.

Factor 0, 86 is applied to power for Cooling calculation: 0, 1521*0, 86= 0.1381 or 13, 81%

- Floor Space

100% of Floor space is occupied.

Figure 41-B-Drosbach Power Usage

Figure 41-C-Cooling Usage

## Capacity Management Kayl

- Overview of racks used / free (physical)

Surface is 206 sqm’s - 70 Racks (16 used / 54 free) - 29, 63% used

Figure 42-Kayl Data Room Plan

- Power / Cooling capacity available

- Power

DC2 TAXUD IT Room “K11-45/48” is powered to N+N and is dual corded or utilises in rack Static Switches (STS).

Maximal power distribution is 1.000 W/sqm.

April Monthly Consumption was = 14.497 kWh on 720h

May used power: (15.448 kWh/744h)/206 = 10,079 kW/sqm or 10,08%

- Cooling

3 x 80kW AHU’s on the feed “A” and 3 x 80kW AHU’s on the feed “B”.

Factor 1 is applied to power for cooling calculation: 10,08%

- Floor Space

100% of Floor space is occupied.

Figure 43-Kayl Yearly Consumption

## Manual Power Consumption Measurements

Manual measurements are taken weekly to verify DC Suppliers kW use measurements.

Manual measurement in <Removed company name>) (done by <Removed nominative data>)

| Date | 30-04.14 | 02-05-14 | 31.05.14 |  |  | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| Feed A |  |  |  |  |  |  |
| KWh | 81,807.00 | 82,590.00 | 93,694.00 |  |  | 11,887.00 |
| Feed B |  |  |  |  |  |  |
| KWh | 68,462.00 | 69,131.00 | 78,600.00 |  |  | 10,138.00 |
|  |  |  |  |  |  | 22,025.00 |

Table 41-Drosbach Manual Measurements

May Monthly Consumption provided by EDH 22.629, 00 kWh

OK – Manual Consumption is a little bit higher (the very small difference is due to the fact   that manual meter readings are done a bit later).

.

Manual measurement in <Removed company name>) (done by <Removed nominative data>))

| Date | 30.04.14 | 02-05-14 | 31.05.14 |  |  | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| Feed A |  |  |  |  |  |  |
| KWh | 50,504.00 | 50,748.00 | 57,278.00 |  |  | 6,674.00 |
| Feed B |  |  |  |  |  |  |
| KWh | 54,014.00 | 54,283.00 | 61,629.00 |  |  | 7,615.00 |
|  |  |  |  |  |  | 14,289.00 |

Table 42-<Removed company name Manual Measurements

May Monthly Consumption provided by eBRC = 15.448 kWh

OK – Manual Consumption is lower (the small difference is perhaps due to the fact that manual meter readings are done a bit sooner)

# Environment control drosbach and Kayl

The report below is based on <Removed company name> /<Removed company name> monthly reporting and controlled by weekly visual checks until <Removed product name> Excel sheet in which the temperature, the humidity and power (starting February 2014) using <Removed product name>. Include ranges, set point and triggers.

## Power Drosbach and Kayl

The report below is based on <Removed company name> and <Removed company name> monthly reporting and controlled by DC Floor Manager weekly visual checks

Figure 51-Power Usage Drosbach/Kayl

## Humidity Drosbach and Kayl

The report below is based on <Removed company name> and <Removed company name> monthly reporting and controlled by DC Floor Manager weekly visual checks

Figure 52-Humidity Usage Drosbach/Kayl

eBRC Hygrometry and Temperature Trends

Figure 53-<Removed company name> Hygrometry and Humidity Trends

## Temperature Drosbach and Kayl

The report below is based on <Removed company name> and <Removed company name> monthly reporting and controlled by DC Floor Manager weekly visual checks.

Figure 54-Temperature Usage Drosbach/Kayl

# Incident Management

## Number of Incidents in Drosbach

In the chart and table below an overview of the total number of incidents opened, logged and closed during the reporting period is shown.

Figure 61-Incidents in Drosbach

## Number of Incidents in Kayl

In the chart and table below an overview of the total number of incidents opened, logged and closed during the reporting period is shown.

Figure 62-Incidents in Kayl

## Critical Incidents / Emergency Incidents

Incidents description.

### <Removed company name> Drosbach

29.05.14

Problem with disk on storage EMC VNX5300 in rack D101.

<Removed Nominative data>: Incident created - Incident SR# 63404628 created by <Removed Nominative data>  contract IM80327

Closed (Install of new disk) on 03.06.14

### <Removed company name> Kayl

29.05.14

Door of rack K210 indicated as open in Tivoli - IM80593

<Removed Nominative data>:: Open and close the door by Floor Manager on 30/05/14

Solved on 30/05/14

# Facility Management

## Number of Facility Requests in Drosbach

Total of facility requests opened and closed during April 2014 (see details below.

Figure 71-Number of Facility Requests In Drosbach

01.04.14	  Electricity statement

02.05.14	  Electricity statement

Assignment Asset Tags

05.05.14	  Inventory of free SFP on NS5400 at Drosbach (for <Removed Nominative data>)

Weekly check

07.05.14	  Verify with <Removed company name>: if possible to displace coppers in rack D107 and D108 (as asked by <Removed Nominative data>:)

08.05.14	  Cabling on M5000 at Drosbach

09.05.14	  Verify inventory for Asset manager

12.05.14	  Preparation for the audit of 16/05

13.05.14	  Weekly check

15.05.14	  Decommission of the temporary switches in the D105 and D106

16.05.14	  Audit <Removed company name>

19.05.14	  Audit activities

21.05.14	  Inventory coppers connections at Drosbach

Conference call with <Removed team name>about thresholds on <Removed product name>'s

Weekly check

22.05.14	  Change of the temperature and humidity thresholds on the <Removed product name>'s

26.05.14	  Installation SSG550M at Drosbach with SY + cabling and test

Displacement of Management switches from row 1 to row 2

28.05.14	  Thermography Control + verification of each lighting system + turnstile

by <Removed company name> (Contract with <Removed company name>)

Test with <Removed team  name>

30.05.14	  Electrical statement

Weekly check

## Number of Facility Requests in Kayl

Total of facility requests opened and closed during April 2014 (see details below).

Figure 72-Number of Facility Requests in Kayl

02.05.14	  Electricity statement + Weekly Check

07.05.14	  Install and test fiber trunks between K101 and K210

13.05.14	  Retry all the doubles keys which was in the safe + Weekly Check

16.05.14 	  Audit <Removed company name>

20.05.14	  Re-cabling of the <Removed product name>'s at Kayl + test

22.05.14	  Change of the temperature and humidity thresholds on the <Removed product name>'s

23.05.14	  Change sensitivity on the 6 racks doors which have problem at Kayl

Weekly Check

Conference call Tivoli team: DGTAXUD - Validating implement of DCIM control systems in Kayl

26.05.14	  Displacement of Management switches from row 1 to row 2

27.05.14	 Thermography Control + verification of each lighting system + turnstile by

<Removed company name> (Contract with <Removed company name>)

30.05.14	  Electrical statement + Weekly check

## Number of Equipment Deliveries in Kayl

The total number of transports closed during the reporting period (see details below).

Figure 73-Number of Deliveries in Drosbach

- 05.05.14  -Delivery of <Removed company name> equipment’s (<Removed product name>)

- 05.05.14  Delivery of <Removed product name> equipment’s

- 07.05.14  Delivery of <Removed product name> power supply

- 08.05.14  Delivery of <Removed product name> modules

- 15.05.14  Delivery from <Removed product name>

## Number of Equipment Deliveries in Kayl

The total number of transports closed during the reporting period (see details above).

Figure 74-Number of Deliveries in Kayl

- 23.05.14  Delivery of labels (AL1, AL2 ...)

## Number of Access Request Tickets Opened/Closed in Drosbach

Figure 75-Number of Access Requests in Drosbach

05.05.14	  Access request for <Removed nominative data>

12.05.14           Access request for: <Removed nominative data>

19.05.14 	  Access request for: <Removed nominative data>

21.05.14      	  Access request for <Removed nominative data>

27.05.14           Access request for  <Removed nominative data>

## Number of Access Request Tickets Opened/Closed in Kayl

Figure 76-Number of Access Requests in Kayl

12.05.14           Access request for: <Removed nominative data>

15.05.14 	  Access request for: <Removed nominative data>

27.05.14           Access request for <Removed nominative data>

21.05.14      	  Access request for <Removed nominative data>

21.05.14      	  Access request for <Removed nominative data>

# Inventory in Drosbach Storage Room

Figure 81-Inventory in Drosbach Storage Room Movements

# Planned Maintenances (DroSbach and Kayl)

## Planned Maintenance Activities in Drosbach

- 3rd  - 31th  May 	Weekly PPM’s (Planned Preventive Maintenance) and plant checks

- Emergency Lighting

- Primary and secondary Chiller water pumps

- Primary and secondary HWS pumps

- Generators inspections

- LV Distribution panels

- Crack’s units

- Chillers

- Ladder safety checks

Risk Factor: LOW

- 3rd  - 31th  May	Monthly elevators maintenance

The Data Centre technical team and their specialist sub-contractors perform monthly elevator maintenance. This normal operational maintenance is done one elevator at a time leaving the other elevator fully functional

Risk Factor: LOW

- 3rd  - 31th  May	 <Removed company name> Deep Cleaning – Technical and IT Halls

<Removed company name> are to carry out a deep clean within UPS Rooms, LV rooms, computer halls, and corridors.

Risk Factor: LOW

Figure 91-Planned Maintenances in Drosbach – April 2014

Yearly Provider maintenance plans in Drosbach

Figure 91-Thirteen months rolling forecast

## Planned Maintenance Activities in Kayl

EBRC Kayl - Planned maintenances for April 2014

| May 5-9th | Static UPS Minor Maintenance & PDU Substation Main Maintenance (feed A & B) | Risk Low |
| --- | --- | --- |
| May 13th May 13th | CRAH units (Computer Room Air Handling) Maintenance (feed A & B) Diesels DUPS and Diesels Short Break (feed A & B) Monthly Test (PPM’s) | Risk Low Risk Low |
| May 13th | DUPS (feed A & B) switching while running | Risk Low |
| May 22th | Lift Elevator Monthly Maintenance | Risk Low |

<Removed confidential data>

Figure 92-Yearly Provider maintenance plans in Kayl

# Conclusions

As each month, a lot of activities had been taken in both DG TAXUD Luxembourg Datacenters during the month of May.

We have pursued Kayl <Removed product name> installation issues (linking and implementation) and resolution of findings generated by last LOT3 audit. Problem is fixed and we are awaiting now replacement parts to be delivered by <Removed company name>.

- Some action points have been continued by <Removed company name> TAXUD DCM

- Interaction  between <Removed company name> and <Removed company name> to finalize a solution concerning CMC installation issue and Rizone Implementation (with <Removed nominative data>

Issue solved concerning large majority of <Removed product name> but it stays around 6 units to be replaced due a production failure at <Removed company name> level.

- <Removed company name> audit realized on 16.05 in both sites. (Final reporting is awaited)

- Continuation of optimization measurements (awaiting a global DG Taxud decision after reception of <Removed company name> final offering).

- Fixed a solution and a planning to solve the problem of <Removed product name> implementation at Kayl  after reordering in a first step:

- Are awaiting from <Removed company name> 6 new <Removed  product name> to finalize issue solving.

-	Once issue will be completely solved, <Removed company name> will finalize implementation of <Removed product name> <Removed product name> (no additional charge to be considered)

-	A half day of training is foreseen when solution will be validated.

-	Continuation of optimization measurements

-	Monthly cleaning of It Rooms by <Removed company name> (Drosbach and Kayl).

No major incident happened and all monitored indicators stayed in the SLA limits.

## Risks from DC Management perspective

No significant or major risks are expected in the coming weeks.

## High Light/ Low light section

No significant high light nor low light points to be developped.

## DOCUMENT HISTORY

### Revision History

| Date of this revision: April 15th 2014 | Date of next revision |
| --- | --- |

| Revision Number | Revision Date | Summary of Changes | Changes marked |
| --- | --- | --- | --- |
| v 0.1 | 14/05/2014 | Initial version | (N) |
| v 0.1 | 15/05/2014 | Reviewed by Internal QAC |  |

### Approvals

This document requires following approvals. Signed approval forms are filed in the Quality section of the PCB.

| Name | Title |
| --- | --- |
| <Removed nominative data> | DC Manager DG TAXUD Luxembourg |
| <Removed nominative data> | DC Floor Manager DG TAXUD Luxembourg |

### Distribution

This document has been distributed to

| Name | Title |
| --- | --- |
| <Removed nominative data> | DG TAXUD Head of ICT Infrastructure and Service Delivery |
| <Removed nominative data> | DG TAXUD Project Manager |
| <Removed nominative data> | DG TAXUD Project Manager |
| <Removed nominative data> | DG TAXUD IT infrastructure management officer |
| <Removed nominative data> | ITSM2 LOT1 Delivery Project Executive |
| <Removed nominative data> | ITSM2 LOT1 Project Executive |
| <Removed nominative data> | ITSM2 LOT1 Project Manager |